## Slide 1
INDUSTRIAL ELECTRICAL & INSTRUMENTATION DESIGN
Cable Tray Routing &
Raceway Engineering
Design standards, fill factors, structural supports, clearances, covers, and underground trenches
NEC 392
NEMA VE 1 / VE 2
IEEE Std 525
IEC 61537
OSHA 1910
Hans Raj | Air Liquide · Engineering Training · October 2026
Notes: Welcome. Today we cover the complete design workflow for cable tray and raceway systems: tray hardware selection, NEC 392 fill limits, voltage segregation, NEMA structural supports, bending radius, covers, trenches, BIM coordination, earthing and the final QA gate.

## Slide 2
TRAINING SCOPE
Core Design Modules
Cable Tray Routing & Raceway Engineering
02
FIELD NOTE
Follow industry codes to avoid construction rework and thermal hazards.
01
Hardware & Selection
Ladder, solid bottom, channel, and wire mesh configurations.
02
NEC Fill Capacity
Cross-section limits, derating, and future reserve space.
03
Segregation Rules
EMI separation between HV, LV, and instrument signals.
04
NEMA Support Spans
Structural load classes and fitting support rules.
Notes: Four modules: hardware selection, NEC 392 fill capacity, EMI segregation, and NEMA structural supports. Everything feeds the final QA checklist before IFC.

## Slide 3
COMPONENT SELECTION
Tray Geometry & Industrial Service
Cable Tray Routing & Raceway Engineering
03
FIELD NOTE
Specify hot-dip galvanized steel, marine-grade 6063-T6 aluminum, or FRP for corrosive environments.
Ladder Tray
9-inch or 12-inch rung spacing.
APPLICATION
Heavy power cables with maximum ventilation.
Solid Bottom / Trough
Continuous metallic base protection.
APPLICATION
Sensitive instrumentation and EMI-shielded lines.
Wire Mesh (Basket)
Field-adaptable lightweight grid.
APPLICATION
Cat6 / fiber telecom, data-center overhead drops.
Channel Tray
3 to 6-inch narrow single-run track.
APPLICATION
Single equipment branch drops from main rack.
Notes: Ladder for heavy power and ventilation; solid bottom for instrumentation and EMI shielding; wire mesh for telecom; channel tray for single branch drops. Material per environment: HDG steel, 6063-T6 aluminum, FRP.

## Slide 4
NEC 392 COMPLIANCE
Tray Fill & Cross-Section Calculations
Cable Tray Routing & Raceway Engineering
04
FIELD NOTE
Sizing check: Required Width ≥ ( Σ Cable OD² × 1.25 ) ÷ Usable Depth — guarantees single-layer spacing when required.
40%
Power Cable Fill Limit
Maximum allowable cross-sectional fill for multi-conductor power under NEC 392.22.
50%
Control & Signal Limit
Maximum usable area for non-heat-generating control and instrumentation lines.
20%
Future Reserve Margin
Mandatory spare width reserved for upcoming plant expansions and revamps.
Notes: NEC 392.22 working limits: 40% fill for multiconductor power, 50% for control/signal, and hold 20% spare capacity for future expansion. The width formula is an area method with a 1.25 packing margin.

## Slide 5
INSTALLATION GEOMETRY
Laying Arrangement: Single-Core vs Multi-Core
Cable Tray Routing & Raceway Engineering
05
FIELD NOTE
Incorrect single-core bundling creates hazardous circulating currents and severe tray overheating.
Single-Core Cables
Trefoil Formation — Route in grouped trefoils to balance induced magnetic fields.
Single-Layer Rule — Strictly no multi-layer stacking; space groups by 2 × cable diameter.
Short-Circuit Cleating — Rated cleats every 1.5 m to withstand dynamic electromagnetic forces.
Non-Magnetic Clamps — Stainless steel or aluminium hardware to stop eddy-current heating.
Multi-Core Cables
Flat Side-by-Side — Low-voltage power placed touching, or spaced by 1 × cable diameter.
Thermal Stacking — Avoid multi-layer stacking unless ampacity derating is applied.
Direct Tie Fastening — UV-resistant heavy nylon or coated steel ties on rungs.
Vertical Rung Anchoring — Support multi-core every 450 mm on vertical risers.
Notes: Single-core AC circuits must run in trefoil with non-magnetic cleats — bundling them wrong induces circulating currents and overheating. Multi-core runs flat, single layer, derated if stacked.

## Slide 6
ELECTROMAGNETIC COMPATIBILITY
Voltage Segregation & Separation Distances
Cable Tray Routing & Raceway Engineering
06
FIELD NOTE
Maintain 90° right-angle crossings wherever signal trays must cross power routes.
Tray Level / Class | Voltage Level | Vertical Separation | Physical Divider Rule
Top Tier (Tier 1) | High Voltage (> 1 kV to 33 kV) | Top position | Separate tray; no shared services
Tier 2 | Low Voltage Power (< 1 kV) | 300 mm from HV | Solid metallic barrier if in same tray
Tier 3 | Control & Interlocking (110 V / 230 V) | 250 mm from LV | Perforated barrier minimum
Bottom Tier (Tier 4) | Analog & Fieldbus (< 50 V / 4–20 mA) | 450 mm from power | Dedicated solid-bottom tray or conduit
Notes: Vertical tier order: HV on top, then LV power, control, and analog/fieldbus at the bottom, with the separations shown. Where trays must cross, do it at 90 degrees to minimise coupling.

## Slide 7
STRUCTURAL ENGINEERING
NEMA VE 1 / VE 2 Support Standards
Cable Tray Routing & Raceway Engineering
07
FIELD NOTE
Thermal expansion: install expansion splice plates every 30 m on straight outdoor aluminium runs.
splice @ 0.25 L
support span L (12 ft / 20 ft class)
NEMA Load Class Ratings
Class 12C (100 lb/ft @ 12 ft span) or 20C (100 lb/ft @ 20 ft). Factor wind, ice, and a 200 lb concentrated worker load.
Splice Joint Location — 0.25 L Rule
Locate splice connectors at quarter-span distance from the support beam. Never place splices at mid-span.
NEMA VE 2 Fitting Support
Support within 600 mm (2 ft) of each horizontal bend, tee, cross, or vertical reducer fitting.
Notes: NEMA class = load per foot at a given span: 12C is 100 lb/ft at 12 ft. Add wind, ice and a 200 lb worker point load. Splices go at quarter span — never mid-span where bending moment peaks. Fittings get a support within 600 mm.

## Slide 8
INSTALLABILITY & ERGONOMICS
Substation & Switchgear Room Clearances
Cable Tray Routing & Raceway Engineering
08
FIELD NOTE
Comply with OSHA 1910 headroom and maintain a 2.1 m clear walkway below the bottom rack.
300 mm (12 in) Top Headroom
Overhead clearance above the tray side rail for cable pulling and roller guides.
600 mm (24 in) Side Access
Clear pathway between tray edge and wall or structural columns for personnel.
Switchgear Dropping Corridor
Align overhead trays with panel top-entry plates to avoid sharp S-bends.
300 mm
600 mm
2.1 m
walkway
Notes: Three clearances to defend in layout reviews: 300 mm above the rail for pulling gear, 600 mm personnel access beside the tray, and 2.1 m headroom below the bottom rack per OSHA 1910.

## Slide 9
PULLING STRESS & FITTINGS
Cable Minimum Bending Radius (MBR)
Cable Tray Routing & Raceway Engineering
09
FIELD NOTE
Fitting radius rule: R fitting ≥ MBR of the largest cable in the tray.
CLASS 1
6 × OD
Control / Signal
Unarmored instrument pairs; select 300 mm fitting radius.
CLASS 2
8–12 × OD
LV Power
Armored & unarmored LV; select 450 mm fitting radius.
CLASS 3
12–15 × OD
MV / HV Shielded
Medium-voltage tape shield; specify 600–900 mm fitting radius.
CLASS 4
20 × OD
Optical Fiber
Dynamic pulling limit to prevent internal glass micro-fractures.
Notes: Minimum bending radius scales with cable construction — from 6×OD for unarmored instrument pairs up to 20×OD for optical fiber during pulling. Tray fitting radius must meet or exceed the largest cable's MBR.

## Slide 10
ENVIRONMENTAL & THERMAL DESIGN
Cable Tray Cover Philosophy
Cable Tray Routing & Raceway Engineering
10
FIELD NOTE
Specify heavy-duty stainless steel cover hold-down clamps rated for local design wind velocities.
01
Peaked / Flanged Covers
Pitched profile sheds rainwater, snow, and chemical process deposits outdoors.
USE Outdoor racks & pipe bridges
02
Mechanical Protection
Solid covers mandatory within 1.8 m of platforms, stairs, and crane lift corridors.
USE Falling tool & slag zones
03
Ampacity Derating
Solid unventilated covers trap heat, penalizing cable ampacity by 10% to 15%.
DERATING Apply 0.85 – 0.90 factor
04
Raised Standoff Spacers
25–50 mm raised cover brackets restore convective airflow while blocking sunlight.
FIX Avoids thermal choke points
Notes: Covers are a trade-off: they protect outdoors and under platforms, but solid covers cost 10–15% ampacity. Raised standoff spacers give sun/debris protection while keeping convective cooling.

## Slide 11
CIVIL & SUBSTATION INTERFACE
Underground Cable Trench Standards
Cable Tray Routing & Raceway Engineering
11
FIELD NOTE
Segregate MV power on one side wall and control / instrumentation on the opposing trench wall.
Precast Trench & 1:100 Bed Slope
Reinforced concrete with continuous longitudinal slope towards sumps to eliminate standing water.
Wall-Mounted Cable Racking
Unistrut cantilever brackets along walls; bottom cable level raised ≥ 100 mm off the trench floor.
Cover Class & Entry Seals
Heavy RCC / chequered covers for roads; fire-rated gas-tight transits at building entry walls.
RCC / chequered cover
MV power wall
Instrument wall
1:100 slope → sump
Notes: Trench rules: precast RCC with a 1:100 fall to sumps, cables racked on walls at least 100 mm off the floor, MV and instrumentation on opposite walls, heavy covers at road crossings and gas-tight transits into buildings.

## Slide 12
DIGITAL ENGINEERING WORKFLOW
BIM / 3D Clash Coordination
Cable Tray Routing & Raceway Engineering
12
FIELD NOTE
Conduct clash tests at 0 mm tolerance for structural steel and 25 mm for insulated piping.
Clash detection — structural vs MEP (image: united-bim.com)
Piping Right-of-Way Rules
Route cable trays ABOVE steam, hydrocarbon, and slurry pipes to eliminate leak-dripping hazards.
HVAC Duct Clearances
Maintain 150 mm minimum separation from chilled-air ducts to stop surface thermal condensation.
Zero Soft Clashes
Model cable pull envelopes and maintenance zones directly in Revit / Navisworks models.
Notes: In the 3D model: trays go above leak-prone piping, 150 mm off chilled ducts, and we model pull envelopes and maintenance space as objects so soft clashes are caught before construction.

## Slide 13
SAFETY & INTEGRITY
Earthing, Bonding & Grounding (NEC 250)
Cable Tray Routing & Raceway Engineering
13
FIELD NOTE
Remove paint, anodized coating, and lacquer completely at all bonding contact lugs.
Bonding Jumpers
Flexible copper braid jumpers across every expansion joint, swivel, and reducer.
Main Grid Taps
Connect tray spine to the main earthing ring at 20 m intervals using 70 mm² bare copper.
Low Resistance Limit
Measure end-to-end path resistance; must not exceed 0.1 Ω per IEEE Std 525.
Equipment Grounding
Tray cannot substitute for the dedicated EGC green wire in branch circuits.
Notes: Grounding continuity: braid jumpers at every mechanical break, earthing-ring taps every 20 m with 70 mm² bare copper, verified below 0.1 ohm end-to-end, and the tray never replaces the equipment grounding conductor.

## Slide 14
QUALITY ASSURANCE
Design Review & QA/QC Gate Checklist
Cable Tray Routing & Raceway Engineering
14
FIELD NOTE
Complete sign-off by the Lead Electrical Engineer prior to issuing drawings for construction (IFC).
✓
Fill Verification
Cross-sectional fill verified ≤ 40% (power) and 50% (control) with 20% spare.
✓
Fitting Radius Validation
Tray bend radii ≥ minimum bending radius of the thickest cable.
✓
Segregation Matrix
HV, LV, and instrumentation lines placed on correct vertical tiers.
✓
Support Calculations
Structural spans validated under NEMA VE 1 with the 0.25 L splice rule.
✓
Cover & Trench Compliance
Outdoor peaked covers, ampacity derating, and trench drains checked.
✓
Penetration Details
2-hour UL-listed firestops and gas barrier seals scheduled on the MTO.
Notes: Six gates before IFC: fill, bending radius, segregation tiers, support spans, covers/trench, and fire-stopped penetrations — signed off by the Lead Electrical Engineer.

## Slide 15
ENGINEERING TRAINING COMPLETE
Thanks & Discussion
Safe raceway design balances electrical segregation, structural loading, thermal derating, and constructability in field execution.
REFERENCE STANDARDS
NEC 392
NEMA VE 1 / VE 2
IEEE Std 525
IEC 61537
OSHA 1910
Hans Raj | Air Liquide
Notes: Open the floor for questions; recap the four pillars: segregation, structure, thermal, constructability.

## Slide 16
APPENDIX
Image Sources
Cable Tray Routing & Raceway Engineering
16
BIM clash detection render (slide 12):
https://www.united-bim.com/wp-content/uploads/2019/04/Clash-detection-for-hotel-project-of-structural-and-MEP.jpg
Source: www.united-bim.com
All diagrams are original vector illustrations created for this training deck.