## Slide 1
LADDER TRAY RUN · SIDE ELEVATION
SPAN S = 3.66 m (12 ft, CLASS C)
RUN LENGTH L
SEVEN CABLES · ONE LAYER · LOAD CLASS C
INDUSTRIAL ELECTRICAL & INSTRUMENTATION DESIGN
Cable Tray Routing
& Raceway Engineering
Design standards, fill factors, structural supports, clearances, covers and
underground trenches
DESIGN BASIS
NEC 392
NEMA VE 1 / VE 2
IEEE 525
IEC 61537
Field engineering training
29 October 2026
Trainer: Hans Raj
Notes: Welcome. This is a working session, not a lecture: every rule ends with what it looks like on site. By the end you should be able to size a tray, pick a support class, and pass a drawing through QA without a rework loop.

## Slide 2
AGENDA
Four modules, one deliverable
Each module answers one question the drawing has to survive: what is the system, what size is it, will it stand, and is it safe
and checkable.
01
Foundations
System anatomy, tray types, material selection.
Slides 4–8
02
Electrical sizing & segregation
Fill limits, worked sizing, tier separation, laying, derating.
Slides 9–14
03
Structural & installation
NEMA load classes, supports, clearances, bend radii, expansion.
Slides 15–19
04
Safety, QA & digital
Earthing and bonding, clash coordination, QA gate, recap.
Slides 20–25
How to use this session
Rules are grouped by the standard that owns them —
the tag tells you where to look it up.
Every red number is a hard limit; every amber note is
good practice, not code.
The closing recap is the page to photograph before
you leave.
4
MODULES
25
SLIDES
45
MINUTES
Cable Tray Routing & Raceway Engineering · Industrial E&I Design
02 / 25
Notes: Point out the colour code early: blue = design rule, red = hard limit, amber = engineering practice we adopt but the code does not mandate. That distinction is the single biggest source of arguments in design reviews.

## Slide 3
LEARNING OUTCOMES
By the end of this session you can…
Four things a designer or supervisor should be able to do unaided tomorrow morning.
01
Choose the tray
Pick ladder, trough, wire-mesh or
channel for a given cable mix, and
justify it in one sentence.
SELECTION
02
Size it to code
Apply NEC 392 fill limits, run the
sum-of-squares width check, and
show the reserve margin.
NEC 392
03
Support it
Set the NEMA VE-1 load class and
span, place splices and fitting
supports correctly.
NEMA VE-1/2
04
Prove it
Walk a drawing through the six QA
gates — fill, radius, segregation,
supports, covers, penetrations.
QA GATE
Cable Tray Routing & Raceway Engineering · Industrial E&I Design
03 / 25
Notes: Name the four outcomes and tell them these map to the four QA gates the checker will use. If they can do these four, they can sign a tray drawing.

## Slide 4
01
Foundations
What the tray system is, what it costs when it is wrong, and how to choose type and
material.
IN THIS MODULE
Why the code exists — the failure modes behind each rule.
Anatomy of a tray run: tray, support, splice, bonding,
cover.
Tray types and where each one is the wrong answer.
Material selection including galvanic-pair traps.
01
Foundations
02
Electrical sizing
03
Structural
04
Safety & QA
04 / 25
Notes: Ten minutes. The goal is vocabulary, so the rest of the session is not a glossary exercise.

## Slide 5
WHY THIS MATTERS
A tray run is cheap to design and expensive to fix
Three failure modes drive every rule in this deck. Each one is discovered late, after concrete, steel or cable is already installed.
10–15%
Lost ampacity
A solid cover or four stacked layers can cost
10–15% of current-carrying capacity. The cable
is derated, the breaker is not — so the circuit
fails thermally, not electrically.
THERMAL
1 width
The rework loop
One tray width short and every downstream
support, penetration and firestop is redrawn.
Sizing once with a 20% reserve is cheaper than
a change order.
COST
6 gates
What QA catches
Fill, radius, segregation, supports, covers,
penetrations. A missed gate typically surfaces
during installation, when the cable is already
pulled.
SCHEDULE
Rule of thumb: the drawing should prove four things — it fits, it stands, it is separated, and it is bondable.
Cable Tray Routing & Raceway Engineering · Industrial E&I Design
05 / 25
Notes: Do not spend long here. One sentence per failure mode. The point: every later rule has a body count.

## Slide 6
SYSTEM ANATOMY
Every run is five decisions, not one
A tray line on a drawing is really five separate decisions — and each has its own standard, its own limit and its own QA check.
1
2
3
4
5
TYPICAL ELEVATION · NOT TO SCALE
FIVE DECISIONS
1
Tray section
Type, width, depth, material — NEC 392 + NEMA VE-1
2
Support
Load class, span, cantilever or trapeze — NEMA VE-1
3
Splice
Location rule: between support and quarter point
4
Bonding
Electrical continuity — NEC 250.96 / 392.60
5
Cover
Weather, mechanical protection, derating trade-off
Cable Tray Routing & Raceway Engineering · Industrial E&I Design
06 / 25
Notes: Walk the numbered callouts on the drawing. Five decisions; if the drawing does not state all five, it is not a construction drawing yet.

## Slide 7
COMPONENT SELECTION
Four tray families and where each belongs
Geometry decides ventilation, support continuity and EMI behaviour. Pick by cable mix first, then by environment.
Ladder
Rung spacing 229 / 305 mm (9 /
12 in)
Heavy power cables with maximum
ventilation and easy tie-off.
USE
Long power runs, cable ladders on
racks
AVOID
Small signal cables — they sag between
rungs
Solid bottom / trough
Continuous metallic base
Full support for small cables and a
metallic shield when bonded at both
ends.
USE
Instrumentation, control, sensitive
signals
AVOID
Uncapped outdoors — it holds water
Wire mesh
Field-adaptable grid, light
weight
Fast to route and re-route; excellent
for data and fibre drops.
USE
Cat6 / fibre, data-centre overhead
AVOID
Heavy power — deflection and no
shielding
Channel
75–150 mm (3–6 in) narrow track
A single narrow run for a small,
known cable group.
USE
Single equipment branch drops
AVOID
Mixed voltages without a divider
Cable Tray Routing & Raceway Engineering · Industrial E&I Design
07 / 25
Notes: Ask the room: which tray for a 33 kV feeder? Which for a 4–20 mA loop? The answer must name the reason, not the name.

## Slide 8
MATERIAL SELECTION
Material is a corrosion decision, then a cost decision
Default is hot-dip galvanised steel. Everything else has to earn its place with an environment.
MATERIAL
ENVIRONMENT / USE
STRENGTHS
WATCH OUT FOR
Hot-dip galv. steel (HDG)
General outdoor, industrial, coastal with coating
Cheapest robust default; covers NEMA load
classes A–C
Coating damage at cut ends — repair with
zinc-rich paint
Stainless 304 / 316L
Chemical plant, chlorides, washdown
No coating to repair; 316L for chloride
Cost; galvanic isolation from carbon steel
Aluminium 6063-T6
Clean indoor, long lightweight runs
Light, no painting, good with aluminium cable
Bare copper in contact = galvanic
corrosion; not for chloride
FRP / composite
Very corrosive, EMC-neutral areas
Non-conductive, chemically inert
Lower stiffness — closer supports; UV
degradation
Galvanic rule: separate dissimilar metals with a plated barrier, and never lay bare copper EGC in an aluminium tray.
Grades and finishes to be confirmed against the project material specification.
Cable Tray Routing & Raceway Engineering · Industrial E&I Design
08 / 25
Notes: Emphasise the galvanic pairing rule — it appears again in the earthing module and it is the most common site defect.

## Slide 9
02
Electrical sizing & segregation
Fill limits, a worked sizing example, voltage segregation, laying geometry and thermal
derating.
IN THIS MODULE
NEC 392 fill limits — including the solid-bottom case most
people miss.
A worked width calculation from cable list to a purchased
tray size.
Voltage segregation and the EMI rules behind the tier table.
Laying geometry, cleating and thermal derating.
01
Foundations
02
Electrical sizing
03
Structural
04
Safety & QA
09 / 25
Notes: The heart of the session. Slow down on the worked example — that is the skill they will use every week.

## Slide 10
NEC 392.22 · FILL
Fill limits are heat limits
The percentages exist so cables can shed heat. They are a limit on the sum of cable cross-sections against the usable interior area.
%
0
15
30
45
60
40
Power &
lighting
hard limit
50
Control &
signal
hard limit
35
Solid-bottom
tray
stricter
20
Reserve
(practice)
not code
40% — power and lighting
Multi-conductor power cables rated ≤ 2000 V in ladder or ventilated trough tray.
NEC 392.22(A)
50% — control and signal
Control, instrumentation and similar cables. Mixed trays use the stricter limit per cable type.
NEC 392.22(A)
20% future reserve
Not a code requirement. It is the margin that keeps the next revamp from becoming a re-route.
PRACTICE
Solid-bottom and covered trays trap heat: NEC applies stricter fill and manufacturer derating applies on top.
Cable Tray Routing & Raceway Engineering · Industrial E&I Design
10 / 25
Notes: Common exam point: nobody remembers the solid-bottom value (35%). Also make clear that 40/50 are code, 20% is us.

## Slide 11
WORKED EXAMPLE · TRAY WIDTH
From cable list to a purchased width in four steps
Single-layer assumption. OD = overall diameter from the cable datasheet.
W ≥ Σ(OD²) ÷ usable depth
× 1.25 reserve
CABLE LIST
CABLE
QTY
OD (MM)
OD²
Σ OD² (MM²)
3C × 95 mm² LV
8
45
2 025
16 200
Required inside width
162 mm
With 1.25 reserve
203 mm
Selected tray
300 mm × 100
mm
The sum-of-squares method is a single-layer rule of thumb: it fails if cables are stacked or if any OD exceeds the usable depth.
1
List cables
8 × 3C × 95 mm² LV power, OD 45 mm. Usable depth of a 4 in tray: 100 mm.
2
Square and sum
Σ OD² = 8 × 45² = 8 × 2 025 = 16 200 mm².
3
Divide by depth
16 200 ÷ 100 = 162 mm minimum inside width.
4
Apply reserve, round up
162 × 1.25 = 203 mm → select the next standard width: 300 mm tray.
Cable Tray Routing & Raceway Engineering · Industrial E&I Design
11 / 25
Notes: Walk it with a calculator. Stress: this is a thumb rule for one layer — if the run needs two layers, go back to the NEC area method.

## Slide 12
ELECTROMAGNETIC COMPATIBILITY
Segregation is a tier order, not a preference
Highest voltage on top, most sensitive signal at the bottom, and a barrier whenever the two share steel.
TIER
SERVICE
VOLTAGE
SEPARATION FROM THE TIER ABOVE
DIVIDER / RULE
1 — top
HV power
> 1 kV to 33 kV
Top position, own tray
No shared services
2
LV power
≤ 1 kV
≥ 300 mm below HV
Solid metallic barrier if shared
3
Control & interlock
110 / 230 V
≥ 250 mm below LV
Perforated barrier minimum
4 — bottom
Analog & fieldbus
< 50 V / 4–20 mA
≥ 450 mm below power
Dedicated solid-bottom tray or
conduit
Where signal and power must cross, cross at 90°. Parallel runs couple; perpendicular crossings do not.
Tier spacing shown is project design practice — NEC does not prescribe tier distances; it prescribes electrical continuity and safe installation.
Cable Tray Routing & Raceway Engineering · Industrial E&I Design
12 / 25
Notes: This is the table people photograph. Make clear the numbers are our project standard, so they can defend them without claiming they are NEC.

## Slide 13
INSTALLATION GEOMETRY
Single-core and multi-core are not laid the same way
Bundling single-core cables the wrong way creates circulating currents and eddy heating; multi-core is mostly about heat and support.
Single-core
Trefoil, one layer, non-magnetic hardware
Trefoil groups balance the induced field in each phase.
One layer only — never stacked; separate groups by 2 × OD.
Non-magnetic clamps (stainless or aluminium) to stop eddy heating.
Cleats: rated for the short-circuit burst — spacing per the SC calculation,
typically ≈ 1.5 m for LV.
Multi-core
Flat, touching, trefoil unnecessary
Lay flat side by side, touching or at 1 × OD for LV power.
Stacking is allowed only with ampacity derating applied.
UV-resistant ties on rungs; no sharp edges under the tie.
Vertical risers: support at ≈ 450 mm on rungs.
Wrong bundling of single-core cables is a design error, not an installation error — it is decided on the drawing.
Cable Tray Routing & Raceway Engineering · Industrial E&I Design
13 / 25
Notes: If someone asks why trefoil: induced voltages in the sheath. Keep it short — the practical rule is one layer, non-magnetic clamps, trefoil groups.

## Slide 14
ENVIRONMENTAL & THERMAL DESIGN
A cover buys weather protection and pays for it in
ampacity
The derating factor multiplies the cable’s tabulated current. Never specify a cover without telling the cable sizing calculation.
×
0
0.275
0.55
0.825
1.1
1.00
Open
ladder
reference
0.95
Ventilated
cover
practical
0.85
Solid
cover
worst case
0.92
Solid +
standoff
recovered
Peaked / flanged cover
Pitched profile sheds rain, snow and process deposits on outdoor racks and pipe bridges.
OUTDOOR
Solid where things fall
Mandatory within 1.8 m of platforms, stairs and crane corridors — falling tools and slag.
PROTECTION
Raised standoff spacers
25–50 mm brackets restore convective airflow while still blocking sunlight.
RECOVERY
Values are indicative engineering practice (≈0.85–0.90 for solid covers); confirm against the cable manufacturer’s derating table and IEEE 525 guidance.
Cable Tray Routing & Raceway Engineering · Industrial E&I Design
14 / 25
Notes: Key message: the cover decision is a cable-sizing decision. If the cover is added after sizing, the cable may be undersized.

## Slide 15
03
Structural & installation
NEMA load classes, support spacing, clearances, bend radii and thermal expansion.
IN THIS MODULE
NEMA VE-1 load classes and what the letters actually
mean.
Support and splice placement, including the 0.25 L rule.
Clearances that make the run buildable.
Bend radius and thermal expansion.
01
Foundations
02
Electrical sizing
03
Structural
04
Safety & QA
15 / 25
Notes: Structural module. The two rules that get remembered: quarter point splice, and fitting support within 600 mm.

## Slide 16
STRUCTURAL ENGINEERING · NEMA VE-1 / VE-2
The load class is a span and a weight, read together
Class designation = support span in feet + working load designation. Tested as a simple span with a 1.5 safety factor.
12C
12 ft (3.66 m)
100 lb/ft (149 kg/m)
Class C = 100 lb/ft working load
20C
20 ft (6.09 m)
100 lb/ft (149 kg/m)
Same load over a longer span → heavier
section
A / B
8–20 ft
50 / 75 lb/ft
A = 50 lb/ft, B = 75 lb/ft
NEMA VE-1
1.5 safety factor
A 100 lb/ft tray is proven at 150 lb/ft. Newer editions mark
rated load and span directly instead of the letter code.
NEMA VE-2 §4.3.1
Splice at the quarter point
Keep joints between the support and the quarter point; never
at mid-span or directly over a support. One splice between
supports.
NEMA VE-2 §4.4.1
Support the fittings
Horizontal elbows, tees, crosses and reducers supported
within 600 mm (2 ft) of each fitting extremity.
Project spec may add a concentrated load case (commonly 200 lb / 90 kg at mid-span) plus wind and ice — that is a specification requirement, not a NEMA class.
Cable Tray Routing & Raceway Engineering · Industrial E&I Design
16 / 25
Notes: Correct the common belief that the letter is a strength grade. It is a working-load designation; the number is the span.

## Slide 17
INSTALLABILITY & ERGONOMICS
If it cannot be built, it is not designed
Three clearances decide whether the installer can pull cable and whether the operator can walk underneath.
300 mm
TOP HEADROOM
Clear above the side rail for pulling rollers and
cable guides.
600 mm
SIDE ACCESS
Between the tray edge and wall or column, for
hands and tools.
2.1 m
WALKWAY
Clear below the lowest tray. OSHA
walking-working surfaces baseline is 2.03 m (6
ft 8 in).
ALSO ON THE DRAWING
Align overhead trays with switchgear top-entry plates — an S-bend at the panel is a pulling problem and an inspection problem.
Keep tray out of crane lift corridors and away from relief-valve discharge paths.
Reserve the maintenance zone on the drawing, not in the installer’s imagination.
Cable Tray Routing & Raceway Engineering · Industrial E&I Design
17 / 25
Notes: Supervisors feel these numbers immediately. Ask them what clearance they actually get on site — it is usually less.

## Slide 18
PULLING STRESS & FITTINGS
The fitting has to be at least as generous as the cable
Rule: R_fitting ≥ MBR_max, where MBR is the minimum bending radius of the stiffest cable in the run.
R fitting ≥ MBR (max) = k × OD
CABLE CLASS
MBR FACTOR K
TYPICAL FITTING RADIUS
WHY
Control / signal
6 × OD
300 mm
Small conductors, tight but still safe
LV power
8–12 × OD
450 mm
Armoured and unarmoured LV power
MV / HV shielded
12–15 × OD
600–900 mm
Tape shield damage = partial discharge
Optical fibre
20 × OD (pulling)
Per cable data
Internal glass micro-fracture
Bend radius is a cable property. If the fitting radius is not on the drawing, the installer will build what the tray catalogue offers.
Factors are typical values — always use the cable manufacturer’s MBR for the actual cable, and the larger value for the run.
Cable Tray Routing & Raceway Engineering · Industrial E&I Design
18 / 25
Notes: Shielded MV cable is where this bites: too tight a bend and you get partial discharge months later.

## Slide 19
OUTDOOR RUNS · THERMAL MOVEMENT
Long runs move — plan where they move
Aluminium expands about twice as much as steel. On a 100 m outdoor run the movement is real, and it has to happen somewhere.
01
DESIGN
Expansion splice plates
Provide expansion joints on long straight runs and at building transitions;
the gap is set from the installation temperature. Commonly a joint every
~30 m on aluminium — confirm with the manufacturer.
02
NEMA VE-2
Anchor at the middle
Anchor the tray between expansion plates at the support nearest
mid-length; allow movement at all other supports. Support within 600 mm
of each side of an expansion plate.
03
NEC 250.96
Bond across the joint
Every expansion plate breaks the metallic path. A bonding jumper sized per
NEC 250.102 must bridge it, or continuity is lost.
04
DETAIL
Never bolt it solid
A clamped expansion plate becomes a buckle point. Slotted holes and the
specified hardware, not a bolted splice.
Cable Tray Routing & Raceway Engineering · Industrial E&I Design
19 / 25
Notes: This is the slide that prevents the 'why is my tray wavy in July' question. Emphasise bonding across the joint — continuity is the electrical part of a mechanical joint.

## Slide 20
04
Safety, QA & digital deliverable
Earthing and bonding, BIM clash coordination, the QA gate, and the numbers to
remember.
IN THIS MODULE
Earthing and bonding — what the tray may and may not be.
Clash coordination rules in the 3-D model.
The six-gate QA checklist before IFC issue.
The numbers to carry in your pocket.
01
Foundations
02
Electrical sizing
03
Structural
04
Safety & QA
20 / 25
Notes: Final module. This is where drawings get rejected, so it is worth the time.

## Slide 21
SAFETY & INTEGRITY · NEC 250.96 / 392.60
A metal tray is bonded metal first, and an EGC only if it is
qualified
Every metallic tray must be grounded regardless. Whether it can carry fault current as the EGC is a separate, conditional permission.
ALWAYS
Tray sections, fittings and raceways bonded per NEC 250.96 with listed connectors
or jumpers.
Bonding jumpers across expansion plates, adjustable plates and any mechanical
discontinuity.
Remove paint, anodising or lacquer at bonding contact points before making the
connection.
ONLY IF QUALIFIED
Tray may serve as the EGC where it is listed/identified for that purpose and meets
the cross-section rules of NEC Table 392.60(A) — e.g. side-rail area for a ladder
tray.
Otherwise, run a dedicated EGC in every circuit. It is the default, not the exception.
Jumper size per NEC 250.102 / 250.122 — sized from the overcurrent device, not a
fixed 70 mm².
THREE TRAPS FROM THE ORIGINAL DRAFT — NOW FIXED
Bare copper in an aluminium tray
Galvanic corrosion. Use tinned or insulated copper, or a plated
barrier.
“0.1 Ω” as a code limit
That is a project acceptance criterion; IEEE 525 is an
installation guide, not the source of 0.1 Ω.
Tray as EGC on every project
Only where listed and qualified; the drawing must state which
option is used.
Cable Tray Routing & Raceway Engineering · Industrial E&I Design
21 / 25
Notes: Correct the original slide here: the tray CAN be the EGC if qualified, and bare copper in aluminium tray is a defect. Say both plainly.

## Slide 22
DIGITAL ENGINEERING WORKFLOW
Clash coordination is where the routing is actually
decided
The 3-D model is the only place you can check a pull envelope before steel is fabricated.
01
PIPING
Tray above the pipe
Route trays above steam, hydrocarbon and slurry lines so a leak cannot
drip into the tray. Stay out of relief-valve discharge and pipe-break zones.
02
HVAC
150 mm from chilled ducts
Keep clear of chilled-air duct surfaces to avoid condensation on the tray
and on cable jackets.
03
TOLERANCE
0 mm steel, 25 mm insulated pipe
Hard clash against structural steel at 0 mm; 25 mm clearance against
insulated piping (the insulation is the real envelope).
04
ENVELOPE
Model the pull, not just the cable
Model cable-pull envelopes, roller access and the maintenance zone. A
route that is clash-free but unpullable is still a clash.
Cable Tray Routing & Raceway Engineering · Industrial E&I Design
22 / 25
Notes: Push the idea of the pull envelope: most 'no clashes' models are still unbuildable because nobody modelled the space needed to install.

## Slide 23
QUALITY ASSURANCE
Six gates before a drawing goes out as IFC
If a gate fails, the drawing does not leave the office. Each gate maps to a number on the previous slides.
01
Fill verified
≤ 40% power, ≤ 50% control, 35% solid-bottom. Reserve margin shown.
02
Radius validated
Fitting radius ≥ MBR of the stiffest cable in the run.
03
Segregation checked
Tier order and separations correct; barriers scheduled where tiers share steel.
04
Supports calculated
NEMA class and span justified; splices at quarter point; fittings supported within
600 mm.
05
Covers & trench
Outdoor covers, derating applied to cable sizing, trench slope and drains
detailed.
06
Penetrations
Firestops and gas-tight transits listed on the MTO with the seal type.
Released for construction only after the Lead Electrical Engineer signs the gate sheet.
QA GATE · IFC
Cable Tray Routing & Raceway Engineering · Industrial E&I Design
23 / 25
Notes: Hand out the six gates as a one-pager. The signature line is the point: somebody's name is on the drawing.

## Slide 24
RECAP · THE PAGE TO PHOTOGRAPH
Twelve numbers and ten words
If you remember nothing else from today, remember these.
40%
power fill
50%
control fill
35%
solid-bottom fill
20%
reserve (practice)
1.25
sizing reserve factor
0.25 L
splice location
600 mm
fitting support
1.5
NEMA safety factor
300 mm
top headroom
600 mm
side access
90°
power / signal crossing
0.85–0.90
solid-cover derating
THE TEN WORDS
Fill
cable area ÷ usable tray area
MBR
minimum bending radius
EGC
equipment grounding conductor
IFC
issued for construction
MTO
material take-off
HDG
hot-dip galvanised
Trefoil
three single cores in a triangle
UDL
uniformly distributed load
Derating
reducing ampacity for heat
Tier
vertical level in a rack
Cable Tray Routing & Raceway Engineering · Industrial E&I Design
24 / 25
Notes: Ask them to photograph this slide. Then quiz: what is the solid-bottom fill? (35%.) What is the splice rule? (quarter point.)

## Slide 25
ENGINEERING TRAINING COMPLETE
Thanks — questions and site
cases
Safe raceway design balances electrical segregation, structural loading, thermal derating and
constructability in field execution.
FOUR QUESTIONS TO ASK YOUR OWN DRAWING
Name the tray family and the reason.
Prove the fill with a number.
Show the support class and the splice location.
State which EGC option the drawing uses.
Hans Raj · Industrial E&I Design · Air Liquide
REFERENCE STANDARDS · NEC Article 392 · NEMA VE 1 · NEMA VE 2 · IEEE 525 · IEC 61537 · OSHA 1910.28
Notes: Close with the four questions. If a participant can answer all four about their own area, the training worked.