## Slide 1
AIR LIQUIDE • INDUSTRIAL TRAINING
INDUSTRIAL ELECTRICAL
& INSTRUMENTATION DESIGN
Cable Tray Routing & Raceway Engineering
Design standards, fill factors, structural supports, clearances, covers, and underground trenches
NEC 392
NEMA VE 1 / VE 2
IEEE 525
IEC 61537
Lead Trainer • Electrical Design
Hans Raj • Air Liquide
29 Oct 2026 • Classroom Training • 90 mins + Q&A
29
OCT 2026
LADDER TRAY • 600mm • HDG STEEL
Typical overhead rack • Power & control segregation
Industrial best practices • Real plant case studies • 100% editable deck
01 / 16
AIR LIQUIDE • CONFIDENTIAL • TRAINING ONLY
CABLE TRAY • NEC 392

## Slide 2
TRAINING OVERVIEW
Training Scope
Follow industry codes to avoid construction rework and thermal hazards
4 CORE MODULES
1
⌘
Hardware & Selection
Ladder, solid bottom, channel, and wire mesh configurations.
60 mins • Deep dive
2
▣
NEC Fill Capacity
Cross-section limits, derating, and future reserve space.
60 mins • Deep dive
3
◉
Segregation Rules
EMI separation between HV, LV, and instrument signals.
60 mins • Deep dive
4
⚙
NEMA Support Spans
Structural load classes and fitting support rules.
60 mins • Deep dive
!
Outcome: Participants will be able to size, route, and support cable trays per NEC 392 & NEMA VE 1/VE 2 — ready for IFC drawings without rework.
02 / 16
AIR LIQUIDE • CONFIDENTIAL • TRAINING ONLY
CABLE TRAY • NEC 392

## Slide 3
COMPONENT SELECTION
Tray Geometry & Industrial Service
Specify hot-dip galvanized steel, marine-grade 6063 aluminum, or FRP for corrosive environments
HDG STEEL
ALUM 6063
FRP / GRP
LADDER TRAY
9-inch or 12-inch rung spacing.
Application:
Heavy power cables with maximum ventilation.
600mm
HDG • OUTDOOR
SOLID BOTTOM / TROUGH
Continuous metallic base protection.
Application:
Sensitive instrumentation and EMI shield lines.
300mm
ALU • INDOOR
WIRE MESH (BASKET)
Field-adaptable lightweight grid.
Application:
Cat6 / Fiber telecom, data center overhead drops.
400mm
FRP • OUTDOOR
CHANNEL TRAY
3 to 6-inch narrow single-run track.
Application:
Single equipment branch drops from main rack.
150mm
HDG • INDOOR
03 / 16
AIR LIQUIDE • CONFIDENTIAL • TRAINING ONLY
CABLE TRAY • NEC 392

## Slide 4
NEC 392 COMPLIANCE
Tray Fill & Cross-Section Calculations
NEC 392.22 governs maximum usable area — never compromise on heat dissipation
FORMULA
Tray Width ≥ [∑(Cable OD)² × 1.25] ÷ Usable Depth
Guarantee single-layer spacing when required
40%
40%
Power Cable Fill Limit
Maximum allowable cross-sectional fill for multi-conductor power under NEC 392.22(A).
40% of tray interior
Ladder / ventilated trough: 40% • Solid bottom: 35%
50%
50%
Control & Signal Limit
Maximum usable area for non-heat generating control and instrumentation lines.
50% of tray interior
20%
20%
Future Reserve Margin
Mandatory spare width reserved for upcoming plant expansions and revamps.
Spare capacity
i
Design tip: Always layer power cables flat in a single layer to promote heat dissipation. Never exceed 40% — trapped heat risks insulation damage and fire.
CHECK: Total cable area ÷ Tray interior area × 100 ≤ Limit
04 / 16
AIR LIQUIDE • CONFIDENTIAL • TRAINING ONLY
CABLE TRAY • NEC 392

## Slide 5
INSTALLATION GEOMETRY
Laying Arrangement: 1-Core vs Multi-Core
Single-layer, trefoil & flat configurations per IEEE 525 and site practice
⚠ CRITICAL SAFETY
SINGLE-CORE CABLES
Heavy Power Feeders • Trefoil + Single-Layer
R
Y
B
TREFOIL FORMATION
Grouped trefoils balance induced magnetic fields — prevents circulating currents
1
TREFOIL FORMATION
Route in grouped trefoils to balance induced magnetic fields.
2
SINGLE-LAYER RULE
Strictly no multi-layer stacking; space groups by 2 × Cable Diameter.
3
SHORT-CIRCUIT CLEATING
Rated cleats every 1.5 m to withstand dynamic electromagnetic burst.
4
NON-MAGNETIC CLAMPS
Stainless steel or aluminum hardware to stop eddy heating.
MULTI-CORE CABLES
LV & Control • Flat & Anchored
FLAT SIDE-BY-SIDE
1
FLAT SIDE-BY-SIDE
Low-voltage power placed touching or spaced by 1 × Cable Diameter.
2
THERMAL STACKING
Avoid multi-layer stacking unless ampacity derating is applied.
3
DIRECT TIE FASTENING
UV-resistant heavy nylon or coated steel ties on rungs.
4
VERTICAL RUNG ANCHORING
Support multi-core every 450 mm on vertical risers.
⚠ Incorrect single-core bundling creates hazardous circulating currents and severe tray overheating — never mix 1-core and multi-core without segregation.
05 / 16
AIR LIQUIDE • CONFIDENTIAL • TRAINING ONLY
CABLE TRAY • NEC 392

## Slide 6
ELECTROMAGNETIC COMPATIBILITY
Voltage Segregation & Separation Distances
Per IEEE 525 & NEC 300.3(C) • Maintain 90° right-angle crossovers
Tray Level / Class | Voltage Level | Vertical Separation | Physical Divider Rule
Top Tier (Tier 1) | High Voltage (>1 kV to 33 kV) | Top position | Separate tray; no shared services
Tier 2 | Low Voltage Power (<1 kV) | 300 mm from HV | Solid metallic barrier if in same tray
Tier 3 | Control & Interlocking (110V / 230V) | 250 mm from LV | Perforated barrier minimum
Bottom Tier (Tier 4) | Analog & Fieldbus (<50V / 4-20mA) | 450 mm from Power | Dedicated solid bottom tray or conduit
VERTICAL TIER VIEW
Top = HV → Bottom = Sensitive
TIER 1 HV
>1kV–33kV
300mm
TIER 2 LV POWER
<1kV
250mm
TIER 3 CONTROL
110/230V
450mm
TIER 4 INSTRUMENT
<50V 4-20mA
⚡ HV on TOP • Sensitive at BOTTOM
Maintain minimum 90° right-angle crossovers when signal trays must intersect power routes — never run in parallel without barriers.
Divider: Steel ≥1.6mm or Aluminum ≥2.0mm, full tray depth, bonded both ends
06 / 16
AIR LIQUIDE • CONFIDENTIAL • TRAINING ONLY
CABLE TRAY • NEC 392

## Slide 7
STRUCTURAL ENGINEERING
NEMA VE 1 / VE 2 Support Standards
Safety factor 1.5 • 200 lb concentrated load • Tested per NEMA VE 1 §5.2 / §5.4
NEMA Load Class Ratings
12C / 20C
Class 12C (100 lbs/ft @ 12ft) or 20C (100 lbs/ft @ 20ft). Factor wind, ice, and 200 lb concentrated worker load.
SPAN 12ft → 100 lbs/ft
Support span in feet + load letter: A=50, B=75, C=100 lbs/ft
Splice Joint Location (0.25 L Rule)
0.25 L
Locate splice connectors at 1/4 span distance from support beam. Never place splices at mid-span.
S
SPLICE @ 0.25L
Most vulnerable point — never mid-span
NEMA VE 2 Fitting Support
2 ft / 600mm
Support within 2 feet (600 mm) of each horizontal bend, tee, cross, or vertical reducer fitting.
TEE / BEND ≤ 600mm to support
All fittings need adjacent support
💡 Thermal expansion guide: Install expansion splice plates every 30 m on straight outdoor aluminum runs — aluminum expands ~2× steel.
07 / 16
AIR LIQUIDE • CONFIDENTIAL • TRAINING ONLY
CABLE TRAY • NEC 392

## Slide 8
INSTALLABILITY & ERGONOMICS
Substation & Switchgear Room Clearances
OSHA 1910 + ergonomic pull — keep walkways clear and panels accessible
↑
Top Headroom
300 mm
(12 in)
Required overhead clearance above tray side rail for cable pulling and roller guides.
↑ 300mm pull space
↔
Side Access
600 mm
(24 in)
Clear pathway between tray edge and building wall or structural columns.
← 600mm →
⌖
Switchgear Dropping Corridor
Align with panel top-entry
Align overhead trays directly with panel top-entry plates to avoid sharp s-bends.
Straight drop — no S-bend
OSHA 1910.28 & 1910.303: Comply with headroom and maintain 2.1 m clear walkway below bottom rack at all times — tag obstructions during MC walkdown.
08 / 16
AIR LIQUIDE • CONFIDENTIAL • TRAINING ONLY
CABLE TRAY • NEC 392

## Slide 9
PULLING STRESS & FITTINGS
Cable Minimum Bending Radius (MBR)
Tray fitting radius must never be tighter than the thickest cable — protects insulation & fiber glass
R fitting ≥ MBR max
Specify radius matching largest OD • Use 450–900 mm for MV
Class | Cable Type | MBR (× OD) | Fitting Radius Selection
CLASS 1 | Control / Signal Unarmored instrument pairs | 6 × OD | Select 300 mm fitting radius
CLASS 2 | LV Power Armored & unarmored LV | 8–12 × OD | Select 450 mm fitting radius
CLASS 3 | MV / HV Shielded Medium voltage tape shield | 12–15 × OD | Specify 600–900 mm fitting radius
CLASS 4 | Optical Fiber Glass micro-fracture risk | 20 × OD | Dynamic pulling limit — static 10 × OD
HOW TO CHOOSE
R
Inner edge never < MBR Measure to cable centerline
Tighter bend = higher stress Always upsize the fitting, never downsize the cable spec
CHECK: Verify against manufacturer datasheet before IFC
09 / 16
AIR LIQUIDE • CONFIDENTIAL • TRAINING ONLY
CABLE TRAY • NEC 392

## Slide 10
ENVIRONMENTAL & THERMAL DESIGN
Cable Tray Cover Philosophy
Ventilation vs protection — choose per location, not by habit
Specify heavy-duty stainless steel cover hold-down clamps rated for local design wind velocities
🏔
PEAKED / FLANGED COVERS
Pitched profile sheds rainwater, snow, and chemical process deposits outdoors.
Use: Outdoor racks & pipe bridges
Pitched sheds water
🛡
MECHANICAL PROTECTION
Solid covers mandatory within 1.8 m of platforms, stairs, and crane lift corridors.
Use: Falling tool & slag zones
Solid within 1.8m
🌡
AMPACITY DERATING
Solid unventilated covers trap heat, penalizing cable ampacity by 10% to 15%.
Derating: 0.85–0.90 factor
Heat trap → 10-15% loss
◬
RAISED STANDOFF SPACERS
25–50 mm raised cover brackets restore convective airflow while blocking sunlight.
Fix: Avoid thermal choke points
25-50mm standoff airflow
THERMAL RULE: Without standoff, unventilated cover = 0.85 derating. Always re-check ampacity tables from manufacturer after covering — document on cable sizing sheet.
10 / 16
AIR LIQUIDE • CONFIDENTIAL • TRAINING ONLY
CABLE TRAY • NEC 392

## Slide 11
CIVIL & SUBSTATION INTERFACE
Underground Cable Trench Standards
Drain, rack, seal — trench is civil + electrical interface
Segregate MV vs Control on opposing walls
1
PRECAST TRENCH & 1:100 BED SLOPE
Reinforced concrete with continuous longitudinal slope towards sumps to eliminate standing water.
Slope → sump
SLOPE 1:100 → SUMP
2
WALL-MOUNTED CABLE RACKING
Unistrut cantilever brackets along walls; bottom cable level raised ≥ 100 mm off trench floor.
Cantilever rack ≥100mm
≥100mm off floor
3
COVER CLASS & ENTRY SEALS
Heavy RCC / chequered covers for roads; fire-rated gas-tight transits at building entry walls.
RCC cover + fire transit
FIRE / GAS SEAL
11 / 16
AIR LIQUIDE • CONFIDENTIAL • TRAINING ONLY
CABLE TRAY • NEC 392

## Slide 12
DIGITAL ENGINEERING WORKFLOW
BIM / 3D Clash Coordination
Clash-free before fabrication — Navisworks / Revit MEP coordination
TOLERANCE 0mm steel • 25mm piping
Conduct clash tests at tolerance 0 mm for structural steel and 25 mm for insulated piping
1
Piping Right-of-Way Rules
Always route cable trays ABOVE steam, hydrocarbon, and slurry pipes to eliminate leak dripping hazards.
ABOVE
2
HVAC Duct Clearances
Maintain 150 mm minimum separation from chilled air ducts to stop surface thermal condensation.
150 mm
3
Zero Soft Clashes
Model cable pull envelopes and maintenance zones directly in Revit / Navisworks models.
ENVELOPE
12 / 16
AIR LIQUIDE • CONFIDENTIAL • TRAINING ONLY
CABLE TRAY • NEC 392

## Slide 13
SAFETY & INTEGRITY
Earthing, Bonding & Grounding (NEC 250)
Tray must remain electrically continuous — low resistance fault path
NEC 250 • IEEE 525
1
Bonding Jumpers
Flexible copper braid jumpers across every expansion joint, swivel, and reducer.
✓
2
Main Grid Taps
Connect tray spine to main earthing ring at 20 m intervals using 70 mm² bare copper.
✓
3
Low Resistance Limit
Measure end-to-end path resistance; must not exceed 0.1 Ω per IEEE 525.
✓
4
Equipment Grounding
Tray cannot substitute for dedicated EGC green wire in branch circuits.
✓
Remove paint, anodized coating, and lacquer completely at all bonding contact lugs — bare metal to bare metal. Treat joints with antioxidant compound for aluminum.
13 / 16
AIR LIQUIDE • CONFIDENTIAL • TRAINING ONLY
CABLE TRAY • NEC 392

## Slide 14
QUALITY ASSURANCE
Design Review & QA/QC Gate Checklist
Gate check before IFC — every item must be ticked by Lead Electrical Engineer
SIGN-OFF REQUIRED
Lead Electrical Engineer
✓
Fill Verification
Cross-sectional fill verified ≤ 40% (power) and 50% (control) with 20% spare.
✓
Fitting Radius Validation
Tray bend radii ≥ minimum bending radius of the thickest cable.
✓
Segregation Matrix
HV, LV, and instrumentation lines placed on correct vertical tiers.
✓
Support Calculations
Structural spans validated under NEMA VE 1 with 0.25 L splice rule.
✓
Cover & Trench Compliance
Outdoor peaked covers, ampacity derating, and trench drains checked.
✓
Penetration Details
2-hour UL-listed firestops and gas barrier seals scheduled on MTO.
Complete sign-off by Lead Electrical Engineer prior to issuing drawings for construction (IFC). Keep signed checklist on record for audit.
APPROVED • IFC READY
14 / 16
AIR LIQUIDE • CONFIDENTIAL • TRAINING ONLY
CABLE TRAY • NEC 392

## Slide 15
ENGINEERING TRAINING COMPLETE
Thanks & Discussion
Safe raceway design balances electrical segregation, structural loading, thermal derating, and constructability in field execution.
REFERENCE STANDARDS: NEC 392 • NEMA VE 1/VE 2 • IEEE 525 • IEC 61537 • OSHA 1910
Next Steps
Open floor for site-specific questions • Distribute QA checklist • Issue IFC drawings after sign-off
Q&A
Contact: Hans Raj • hansraj.al@airliquide.com • Lead Electrical Design Air Liquide • Confidential • 29 Oct 2026
Designed for field execution • Editable master • Ready to present
15 / 16
AIR LIQUIDE • CONFIDENTIAL • TRAINING ONLY
CABLE TRAY • NEC 392

## Slide 16
Appendix
Image Sources & References
This deck retains 100% of the original technical content — only visual design and layout have been enhanced.
1
BIM Clash Detection Image
https://www.united-bim.com/wp-content/uploads/2019/04/Clash-detection-for-hotel-project-of-structural-and-MEP.jpg
Source: www.united-bim.com
2
NEC 392, NEMA VE1/VE2, IEEE 525, IEC 61537, OSHA 1910
Official standards publications — refer to latest editions for construction
For detailed fill calculations and load tables, consult manufacturer data sheets (Atkore, Legrand, Schneider)
3
Original cable tray photos & icons
Gemini-generated placeholders replaced with vector illustrations — all text remains editable
Designed in PowerPoint • Editable master • No embedded images for core content
Redesigned by Aarav's AI • 29 Oct 2026 • Designer-grade industrial training deck • All tables & text editable • Built with 2025 premium design system
16 / 16
AIR LIQUIDE • CONFIDENTIAL • TRAINING ONLY
CABLE TRAY • NEC 392